## Sheet1
Town of Cairo Exterior Lighting Upgrade
Notes | Room AND Floor | Manf. | Model | Fixture Type | Existing Fixture Type | Fixt. Qty | Existing Hours | Watts | kW | kWh | Proposed Fixture Type | Fixt. Qty | Proposed Hours | Watts | kW | kWh | kW Saved | kWh Saved
Street Lighting
Within Sidewalk- Height 10' | Main Street | Eiko | LED80WPT50KMOG-G8 | A1 | 250W MH Decorative Post Top | 15 | 4380 | 295 | 4.425 | 19382 | LED Corn Cob Lamp, 80W | 15 | 4380 | 80 | 1.2 | 5256 | 3.23 | 14126
Within Sidewalk- Height 10' | Town Hall | Eiko | LED80WPT50KMOG-G8 | A1 | 250W MH Decorative Post Top | 4 | 4380 | 295 | 1.18 | 5168 | LED Corn Cob Lamp, 80W | 4 | 4380 | 80 | 0.32 | 1402 | 0.86 | 3767
Town Hall
Mounted 10' | North Exterior | Deco | D462-LED-12-50-U-BZ-T | B2 | CFL 23W Globe | 1 | 4380 | 23 | 0.023 | 101 | 12W Led Wallpack w/PE | 1 | 4380 | 12 | 0.012 | 53 | 0.01 | 48
Mounted 5' | Front Exterior | Deco | D462-LED-12-50-U-BZ-T | B6 | CFL PL 13/2 Wallpack | 2 | 4380 | 31 | 0.062 | 272 | 12W Led Wallpack w/PE | 2 | 4380 | 12 | 0.024 | 105 | 0.04 | 166
Mounted 13' | North Exterior | Rab | WP2LED - 49L - 750 - BLANK - U - PCU | B3 | 150W MH Wall Pack | 1 | 4380 | 190 | 0.19 | 832 | 34W LED Wall Pack /PCU | 1 | 4380 | 34 | 0.034 | 149 | 0.16 | 683
Annex Building
Height 8' | Exterior Gooseneck | Philips | PHI 9.5A19/PER/827 | A6 | 11W CFL SI Lamp | 2 | 4380 | 11 | 0.022 | 96 | 10W LED SI Lamp | 2 | 4380 | 10 | 0.02 | 88 | 0 | 9
Senior Center
Height 13' | Exterior Front Door | Rab | WP3LED - 75L -750 - BLANK - U - PCU | A7 | 250W MH Wall Pack | 2 | 4380 | 295 | 0.59 | 2584 | 51W LED Pack /PCU | 2 | 4380 | 51 | 0.102 | 447 | 0.49 | 2137
Height 8' | Exterior Rear Door | Philips | PHI 9.5A19/PER/827 | B3 | 60W Incd. SI Lamp | 1 | 4380 | 60 | 0.06 | 263 | 10W LED SI Lamp | 1 | 4380 | 10 | 0.01 | 44 | 0.05 | 219
Height 6' | Exterior Kitchen Door | Rab | WP1LED - 39L -750 - BLANK - U - PCU | A9 | 100W MH Wall Pack | 1 | 4380 | 128 | 0.128 | 561 | 26W LED Wall Pack /PCU | 1 | 4380 | 26 | 0.026 | 114 | 0.1 | 447
Height 8' | Exterior Front Door | Rab | WP1LED - 39L -750 - BLANK - U - PCU | A6 | 55W CFL Wall pack | 1 | 4380 | 56 | 0.056 | 245.28 | 26W LED Wall Pack /PCU | 1 | 4380 | 26 | 0.026 | 113.88 | 0.03 | 131.4
Height 20' | Exterior Side | Rab | WP3LED - 75L -750 - BLANK - U - PCU | A8 | 90W (2) PAR 38 Lamps | 1 | 4380 | 180 | 0.18 | 788.4 | 51W LED Wall Pack /PCU | 1 | 4380 | 51 | 0.051 | 223.38 | 0.129 | 565.02
Town Park
Height 10' | Garage- Exterior Flood | Rab | WP3LED - 83L -750 - BLANK - U - PCU | A6 | 300W Quartz Hal. Flood- Knuckle Mount | 1 | 4380 | 300 | 0.3 | 1314 | LED Wall Pack w/PCU, 55W | 1 | 4380 | 55 | 0.055 | 241 | 0.25 | 1073
Height 10' | Pavilion Wallpack | Rab | WP3LED - 83L -750 - BLANK - U - PCU | A9 | 250W MH Wall Pack Fixture | 2 | 4380 | 295 | 0.59 | 2584 | LED Wall Pack w/PCU, 55W | 2 | 4380 | 55 | 0.11 | 482 | 0.48 | 2102
Height 25' | Park Entrance- North | Linmore | LL-SL1-XL-400W-50K-T5-UNV-BRN-SF (PC) | B2 | 1000W MH Site Fixture- SF, AA | 1 | 4380 | 1080 | 1.08 | 4730 | LED Site Fixture 400W- SF, AA | 1 | 4380 | 400 | 0.4 | 1752 | 0.68 | 2978
Metal Building- Height 10' | Youth Fair- Exterior Wall Pack | Rab | WP1LED - 39L -750 - BLANK - U - PCU | B9 | 150W MH Wall Pack Fixture | 2 | 4380 | 190 | 0.38 | 1664 | LED Wall Pack w/PCU, 26W | 2 | 4380 | 26 | 0.052 | 228 | 0.33 | 1437
Brick Building- Height 8' | Concession Building- Exterior Wall Pack | Rab | WP1LED - 39L -750 - BLANK - U - PCU | C8 | 100W MH Wall Pack Fixture | 4 | 4380 | 128 | 0.512 | 2243 | LED Wall Pack w/PCU, 26W | 4 | 4380 | 26 | 0.104 | 456 | 0.41 | 1787
Height 10' | Concession Building- Exterior Canopy | Rab | VANLED20W/PCS | C9 | 13W (2) PL Canopy Fixture | 1 | 4380 | 31 | 0.031 | 136 | LED Canopy Fixture w/PCS, 20W | 1 | 4380 | 20 | 0.02 | 88 | 0.01 | 48
Recessed into ground | Flags- uplighting | Philips | 12PAR38/LED/827/F25/DIM/ULW/120 529628 | D1 | 150W Halogen PAR lamp (enclosed) | 3 | 4380 | 150 | 0.45 | 1971 | LED SI Lamp 12W | 3 | 4380 | 12 | 0.036 | 158 | 0.41 | 1813
Recessed into wall | Flags- Walkway | Rab | D462-LED-12-50-U-BZ-T | D2 | 150W Quartz Flood- Knuckle | 1 | 4380 | 150 | 0.15 | 657 | LED Wall Pack w?PC, 12W | 1 | 4380 | 12 | 0.012 | 53 | 0.14 | 604
Highway Dept
Metal Building- mount height approx. 15' | Exterior Wall Pack | Rab | WP3LED - 75L -750 - BLANK - U - PCU | C2 | 90W Par 38 SI Lamp | 2 | 4380 | 180 | 0.36 | 1577 | LED 51W Wall Pack/ PCU | 2 | 4380 | 51 | 0.102 | 447 | 0.26 | 1130
Library
Height 10' | Exterior Soffit | Sylvania | SYL LEDRT8/R3A200UD/940 (SYL EMBB1A8WDC) | B3 | 26W/2 PL 8" Recessed Fixture w/EM | 6 | 4380 | 66 | 0.396 | 1734 | 8" Recessed Fixture w/EM Battery | 6 | 4380 | 23 | 0.138 | 604 | 0.26 | 1130
Height 15' Exterior Front Goosenecks | Exterior Front Goosenecks | Maxlite | 8PLG24QCS | B5 | 26W PL Gooseneck Fixtures | 3 | 4380 | 27 | 0.081 | 355 | LED 8W P- Lamp | 3 | 4380 | 8 | 0.024 | 105 | 0.06 | 250
Ground Level | Walkway Bollards | Philips | 16A21/PER/827 | B6 | 50 MH Bollard Fixture | 4 | 4380 | 72 | 0.288 | 1262 | RL & Hardwire 16W A21 SI Lamp | 4 | 4380 | 16 | 0.064 | 280 | 0.22 | 981
Wastewater Treatment Plant
Wood- wall mounted 12' | Dog Kennel- night light | Rhemphos | RPT-B-TOTALTUBE-T8-G3-4FT-850-A | A2 | 1L4 (28W) T8 Strip Fixture | 1 | 8760 | 23 | 0.023 | 201 | RL & Hardwire 1L4 T8 LED 12W | 1 | 8760 | 12 | 0.012 | 105 | 0.01 | 96
Brick wall- mount 8' | Exterior Driveway | Philips | PHI 9.5A19/PER/827-22/P/E26WG 6/1FB | A3 | 60W Incd. SI Lamp- bell box | 1 | 4380 | 60 | 0.06 | 263 | 10W A19 LED Screw In | 1 | 4380 | 12 | 0.012 | 53 | 0.05 | 210
Brick wall- mount 8' | Exterior Wall Pack | RAB | WP1LED - 39L -750 - BLANK - U - PCU | A4 | 100W MH Wall Pack | 2 | 4380 | 128 | 0.256 | 1121 | 26W LED Wall Pack | 2 | 4380 | 26 | 0.052 | 228 | 0.2 | 894
Brick wall- mount 8' | Exterior entry Door (motion sensor) | Philips | 12PAR38/LED/840/F40/DIM/ULW/121 | A5 | 90W (2) Par38 Flood | 1 | 219 | 180 | 0.18 | 39 | 12W Par38 Screw In | 1 | 219 | 12 | 0.012 | 3 | 0.17 | 37
Pole Mounted 25' | Exterior Water Tanks | Linmore | LL-SL1-MD-150W-50K-T5-UNV-BRN-SF (PC) | A6 | 400W MH Site Light SF 5M AA | 4 | 4380 | 458 | 1.832 | 8024 | 150W Site Light 5M AA Bronze | 4 | 4380 | 150 | 0.6 | 2628 | 1.23 | 5396